{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":38,"n_cols":7,"rows_kept":38,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","4MXM-A9"]
[]
[]
[]
[]
["","","","","","4MXM68A2V1B9","4MXM80A2V1B9"]
["Rozměry","Jednotka","","Výška","mm","734","734"]
["","","","Šířka","mm","974","974"]
["","","","Hloubka","mm","408","408"]
["Hmotnost","Jednotka","","","kg","63","67"]
["Kompresor","Typ","","","","Hermeticky utěsněný rotační kompresor","Hermeticky utěsněný rotační kompresor"]
["Provozní rozsah","Chlazení","Okolí","Min.","°CST","-10","-10"]
["","","","Max.","°CST","46","46"]
["Hladina akustického tlaku","Chlazení","","Jm.","dBA","48","48"]
["","Vytápění","","Jm.","dBA","49","49"]
["Chladivo","Typ","","","","R-32","R-32"]
["","Náplň","","","kg","2","2.4"]
["","Náplň","","","tCO2Eq","1.35","1.62"]
["","Vliv na globální oteplování (GWP)","","","","675","675"]
["Spoje potrubí","Délka potrubí","Max.","OU - IU","m","25 (1)","25 (1)"]
["","Doplňková náplň chladiva","","","kg/m","0,02 (pro délku potrubí přesahující 30m)","0,02 (pro délku potrubí přesahující 30m)"]
["","Rozdíl hladin","IU - OU","Max.","m","15","15"]
["","","IU - IU","Max.","m","7.5","7.5"]
["","Celková délka potrubí","Systém","Skutečná","m","60","70"]
["Standardní příslušenství","Příručka pro instalaci","","","","1","1"]
["","Krytka vypouštění","","","","3","3"]
["","Uzávěr vypouštění","","","","1","1"]
["","Sestava reduktoru","","","","1","1"]
["","Sáček se šrouby","","","","1","1"]
["Energetickou účinná řada","","","","","A+++ ~ D","A+++ ~ D"]
["Napájení","Fáze","","","","1~","1~"]
["","Frekvence","","","Hz","50","50"]
["","Napětí","","","V","220-240","220-240"]
["Poznámky","","","","","(1) - Jedna místnost","(1) - Jedna místnost"]
["","","","","","(2) - Pro kombinaci s CVXM-A, FVXM-A – maximální délka potrubí 30m.","(2) - Pro kombinaci s CVXM-A, FVXM-A – maximální délka potrubí 30m."]
["","","","","","(3) - Viz samostatný výkres s provozním rozsahem","(3) - Viz samostatný výkres s provozním rozsahem"]
["","","","","","(4) - Údaje o elektrickém systému najdete v samostatném výkresu","(4) - Údaje o elektrickém systému najdete v samostatném výkresu"]
["","","","","","(5) - Obsahuje fluorované skleníkové plyny","(5) - Obsahuje fluorované skleníkové plyny"]