{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":96,"n_cols":9,"rows_kept":96,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","ACQ-D"]
[]
[]
[]
[]
["","","","","","ACQ71DV1","ACQ100DV1","ACQ125DV1","ACQ140DV1"]
["Hladina akustického tlaku","Vytápění","","Vysoké","dBA","","44","","47"]
["","","","Jm.","dBA","","41","","44"]
["","","","Tichý provoz","dBA","","36","","41"]
["","","","Nízký","dBA","","38","","43"]
["","Chlazení","","Tichý provoz","dBA","","36","","41"]
["","","","Nízký","dBA","","38","","43"]
["","","","Vysoké","dBA","","44","","47"]
["","","","Jm.","dBA","","41","","44"]
["Standardní příslušenství","Příručka pro instalaci","","","","","Příručka pro instalaci","","Příručka pro instalaci"]
["","Manuální ovládání","","","","","Manuální ovládání","","Manuální ovládání"]
["","Šrouby","","","","","Šrouby","","Šrouby"]
["","Podložka","","","","","Podložka","","Podložka"]
["","Bezdrátové dálkové ovládání","","","","","Bezdrátové dálkové ovládání","","Bezdrátové dálkové ovládání"]
["","Mřížka zámku krytu","","","","","Mřížka zámku krytu","","Mřížka zámku krytu"]
["","Baterie","","","","","Baterie","","Baterie"]
["Control systems","Wired remote control","","","","","ARCWB","","ARCWB"]
["","Infračervené dálkové ovládání","","","","","ARCWLA","","ARCWLA"]
["Připojovací rozměry","Liquid","","OD","mm","","9.52","","9.52"]
["","Plyn","","OD","mm","","15.88","","15.88"]
["","Vypouštění","","","","","19.05","","19.05"]
["Vstup napájení","Chlazení","","Jm.","kW","","0.094","","0.137"]
["","Vytápění","","Jm.","kW","","0.094","","0.137"]
["Hladina akustického výkonu","Chlazení","","","dBA","","56","","60"]
["","Vytápění","","","dBA","","56","","60"]
["Rozměry","Unit","","Width","mm","","820","","820"]
["","","","Depth","mm","","820","","820"]
["","","","Height","mm","","300","","300"]
["Opláštění","Materiál","","","","","Pozinkovaná ocel","","Pozinkovaná ocel"]
["Hmotnost","Unit","","","kg","","39","","39"]
["Ventilátor","Průtok vzduchu","Vytápění","Vysoké","m³/min","","29.2","","34.0"]
["","","","Nízký","m³/min","","21.0","","26.3"]
["","","","Jm.","m³/min","","24.4","","29.2"]
["","","Chlazení","Nízký","m³/min","","21.0","","26.3"]
["","","","Jm.","m³/min","","24.4","","29.2"]
["","","","Vysoké","m³/min","","29.2","","34.0"]
["","","","Tichý provoz","m³/min","","17.6","","22.1"]
["","","Chlazení","Tichý provoz","m³/min","","17.6","","22.1"]
["Ozdobný panel","Hmotnost","","","kg","","4","","4"]
["","Rozměry","","Výška","mm","","82","","82"]
["","","","Hloubka","mm","","990","","990"]
["","","","Šířka","mm","","990","","990"]
["","Barva","","","","","Bílý","","Bílý"]
["Power supply","Fáze","","","","","1~","","1~"]
["","Označení","","","","","V1","","V1"]
["","Frekvence","","","Hz","","50","","50"]
["","Napětí","","","V","","220-240","","220-240"]
["Ventilátor","Průtok vzduchu","Vytápění","Tichý provoz","m³/min","15","","22.1"]
["Vstup napájení","Vytápění","","Jm.","kW","0.067","","0.137"]
["","Chlazení","","Jm.","kW","0.067","","0.137"]
["Ventilátor","Průtok vzduchu","Chlazení","Tichý provoz","m³/min","15","","22.1"]
["Opláštění","Materiál","","","","Pozinkovaná ocel","","Pozinkovaná ocel"]
["Rozměry","Jednotka","","Výška","mm","265","","300"]
["","","","Šířka","mm","820","","820"]
["","","","Hloubka","mm","820","","820"]
["Hmotnost","Jednotka","","","kg","31","","39"]
["Ventilátor","Průtok vzduchu","Chlazení","Vysoké","m³/min","24.4","","34"]
["","","","Jm.","m³/min","20.5","","29.2"]
["","","","Nízký","m³/min","17.6","","26.3"]
["","","Vytápění","Vysoké","m³/min","24.4","","34"]
["","","","Jm.","m³/min","20.5","","29.2"]
["","","","Nízký","m³/min","17.6","","26.3"]
["Hladina akustického výkonu","Chlazení","","","dBA","54","","60"]
["","Vytápění","","","dBA","54","","60"]
["Hladina akustického tlaku","Chlazení","","Vysoké","dBA","41","","47"]
["","","","Jm.","dBA","38","","44"]
["","","","Nízký","dBA","35","","43"]
["","","","Tichý provoz","dBA","32","","41"]
["","Vytápění","","Vysoké","dBA","41","","47"]
["","","","Jm.","dBA","38","","44"]
["","","","Nízký","dBA","35","","43"]
["","","","Tichý provoz","dBA","32","","41"]
["Připojovací rozměry","Kapalina","","Vnější průměr","mm","9.52","","9.52"]
["","Plyn","","Vnější průměr","mm","15.88","","15.88"]
["","Odvod kondenzátu","","","","19.05","","19.05"]
["Dekorační panel","Rozměry","","Výška","mm","82","","82"]
["","","","Šířka","mm","990","","990"]
["","","","Hloubka","mm","990","","990"]
["","Hmotnost","","","kg","4","","4"]
["Řídicí systémy","Infračervené dálkové ovládání","","","","ARCWLA","","ARCWLA"]
["","Kabelové dálkové ovládání","","","","ARCWB","","ARCWB"]
["Standardní příslušenství","Installation manual","","","","Installation manual","","Installation manual"]
["","Wireless remote control","","","","Wireless remote control","","Wireless remote control"]
["","Cover lock grill","","","","Cover lock grill","","Cover lock grill"]
["","Battery","","","","Battery","","Battery"]
["","Operation manual","","","","Operation manual","","Operation manual"]
["","Screws","","","","Screws","","Screws"]
["","Washer","","","","Washer","","Washer"]
["Napájení","Fáze","","","","1~","","1~"]
["","Frekvence","","","Hz","50","","50"]
["","Napětí","","","V","220-240","","220-240"]