{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":75,"n_cols":10,"rows_kept":75,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","ARXS-L"]
[]
[]
[]
[]
["","","","","","ARXS50L2V1B","ARXS71L2V1B","ARXS25L2V1B (Archived)","ARXS35L2V1B (Archived)","ARXS60L2V1B (Archived)"]
["Hladina akustického tlaku","Vytápění","","Vysoké","dBA","","","47","48"]
["","","","Jm.","dBA","","52","","","49"]
["","Chlazení","","Vysoké","dBA","","","46","48"]
["","","","Jm.","dBA","","52","","","49"]
["Standardní příslušenství","Uzávěr vypouštění","","","","","1","1","1","1"]
["","Příručka pro instalaci","","","","","1","1","1","1"]
["","Štítek náplně chladiva","","","","","1","1","","1"]
["","Vícejazyčné štítky pro fluorované skleníkové plyny","","","","","1","1","","1"]
["Chladivo","Charge","","","TCO2Eq","","","2.1","2.5"]
["","Vliv na globální oteplování (GWP)","","","","","2,087.5","2,087.5","2,087.5","2,087.5"]
["","Náplň","","","kg","","1.70","1.0","1.2","1.50"]
["","Type","","","","","R-410A","R-410A","R-410A","R-410A"]
["Motor ventilátoru","Otáčky","Chlazení","Velmi nízké","ot./min","","","780","780"]
["","","Vytápění","Velmi nízké","ot./min","","","740","740"]
["Provozní rozsah","Chlazení","Okolí","Max.","°CDB","","46","46","46","46"]
["","","","Min.","°CDB","","-10","10","10","-10"]
["","Vytápění","Okolí","Max.","° CWB","","18","18","18","18"]
["","","","Min.","° CWB","","-15","-15","-15","-15"]
["Spoje potrubí","Rozdíl hladin","IU - OU","Max.","m","","20.0","15","15","20.0"]
["","Doplňková náplň chladiva","","","kg/m","","0,02 (pro délku potrubí přesahující 10m)","0,02 (pro délku potrubí přesahující 10m)","0,02 (pro délku potrubí přesahující 10m)","0,02 (pro délku potrubí přesahující 10m)"]
["Hladina akustického výkonu","Chlazení","","","dBA","","65","","","62"]
["","Vytápění","","","dBA","","65","","","62"]
["Kompresor","Typ","","","","","Hermeticky utěsněný rotační kompresor","Hermeticky utěsněný rotační kompresor","Hermeticky utěsněný rotační kompresor","Hermeticky utěsněný rotační kompresor"]
["Rozměry","Unit","","Width","mm","","825","765","765","825"]
["","","","Depth","mm","","300","285","285","300"]
["","","","Height","mm","","735","550","550","735"]
["Hmotnost","Unit","","","kg","","47","34","34","47"]
["Ventilátor","Průtok vzduchu","Vytápění","Velmi nízké","cfm","","","904","904"]
["","","","Velmi nízké","m³/min","","","25.6","25.6"]
["","","Chlazení","Velmi nízké","m³/min","","","30.1","30.1"]
["","","","Velmi nízké","cfm","","","1,063","1,063"]
["Power supply","Fáze","","","","","1~","1~","1~","1~"]
["","Frekvence","","","Hz","","50","50","50","50"]
["","Napětí","","","V","","220-230-240","220-240","220-240","220-230-240"]
["Poznámky","","","","","(1) - 220 V","","(1) - Læs specifikationer til den Multi udendørs enhed, der skal tilsluttes, når den er koblet til udendørs enhed i Multi-system.","(1) - Læs specifikationer til den Multi udendørs enhed, der skal tilsluttes, når den er koblet til udendørs enhed i Multi-system."]
["","","","","","(2) - 230V","","(2) - 220 V","(2) - 220 V"]
["","","","","","(3) - 240 V","","(3) - 230V","(3) - 230V"]
["","","","","","","","(4) - 240 V","(4) - 240 V"]
["","","","","","","","(5) - Obsahuje fluorované skleníkové plyny","(5) - Obsahuje fluorované skleníkové plyny"]
["Ventilátor","Průtok vzduchu","Chlazení","Velmi nízké","m³/min","48.9"]
["","","Vytápění","Velmi nízké","m³/min","43.1"]
["","","","Velmi nízké","cfm","1727"]
["","","Vytápění","Velmi nízké","cfm","1522"]
["Rozměry","Jednotka","","Výška","mm","735"]
["","","","Šířka","mm","825"]
["","","","Hloubka","mm","300"]
["Hmotnost","Jednotka","","","kg","47"]
["Motor ventilátoru","Otáčky","Chlazení","Velmi nízké","ot./min","670"]
["","","Vytápění","Velmi nízké","ot./min","670"]
["Kompresor","Typ","","","","Hermeticky utěsněný rotační kompresor"]
["Provozní rozsah","Chlazení","Okolí","Min.","°CDB","10"]
["","","","Max.","°CDB","46"]
["","Vytápění","Okolí","Min.","° CWB","-15"]
["","","","Max.","° CWB","18"]
["Hladina akustického tlaku","Chlazení","","Vysoké","dBA","48"]
["","Vytápění","","Vysoké","dBA","48"]
["Chladivo","Typ","","","","R-410A"]
["","Náplň","","","kg","1.7"]
["","Náplň","","","tCO2Eq","3.5"]
["","Vliv na globální oteplování (GWP)","","","","2087.5"]
["Spoje potrubí","Délka potrubí","Max.","OU - IU","m","30"]
["","Doplňková náplň chladiva","","","kg/m","0,02 (pro délku potrubí přesahující 10m)"]
["","Rozdíl hladin","IU - OU","Max.","m","20"]
["Standardní příslušenství","Installation manual","","","","1"]
["","Drain plug","","","","1"]
["Napájení","Fáze","","","","1~"]
["","Frekvence","","","Hz","50"]
["","Napětí","","","V","220-240"]
["Poznámky","","","","","","(1) - Obsahuje fluorované skleníkové plyny","","","(1) - Obsahuje fluorované skleníkové plyny"]