{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":46,"n_cols":8,"rows_kept":46,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","AZAS-MY1"]
[]
[]
[]
[]
["","","","","","AZAS100M7Y1B","AZAS125M7Y1B","AZAS140M7Y1B"]
["Rozměry","Jednotka","","Výška","mm","990","990","990"]
["","","","Šířka","mm","940","940","940"]
["","","","Hloubka","mm","320","320","320"]
["Hmotnost","Jednotka","","","kg","","70"]
["Kompresor","Type","","","","","Hermeticky utěsněný rotační kompresor"]
["Provozní rozsah","Chlazení","Okolí","Min.","°CST","-5","-5","-5"]
["","","","Max.","°CST","46","46","46"]
["","Vytápění","Okolí","Min.","° CWB","-15","-15","-15"]
["","","","Max.","° CWB","15.5","15.5","15.5"]
["Hladina akustického výkonu","Chlazení","","","dBA","70","71","73"]
["","Vytápění","","","dBA","","71","73 (1)"]
["Hladina akustického tlaku","Chlazení","","Jm.","dBA","53","53","54"]
["","Vytápění","","Jm.","dBA","57","57","57"]
["Chladivo","Typ","","","","R-32","R-32","R-32"]
["","Náplň","","","kg","2.60","2.60","2.90"]
["Chladivo","Vliv na globální oteplování (GWP)","","","","","675"]
["Chladivo","Náplň","","","tCO2Eq","1.76","1.76","1.96"]
["Připojovací rozměry","Kapalina","","Vnější průměr","mm","9.52","9.52","9.52"]
["Piping connections","Plyn","","Vnější průměr","mm","","15.9"]
["Spoje potrubí","Délka potrubí","Max.","OU - IU","m","30","30","30"]
["","","Systém","Ekvivalent","m","50","50","50"]
["","","","Bez náplně","m","30","30","30"]
["","Doplňková náplň chladiva","","","kg/m","Viz instalační příručka","Viz instalační příručka","Viz instalační příručka"]
["","Rozdíl hladin","IU - OU","Max.","m","30.0","30.0","30.0"]
["","","IU - IU","Max.","m","0.5","0.5","0.5"]
["Standardní příslušenství","Installation manual","","","","1","1","1"]
["","Refrigerant label for F-gas regulation","","","","1","1","1"]
["","General safety precautions","","","","1","1","1"]
["","LOT10 Energy Label","","","","1","1","1"]
["","Tie-wraps","","","","2","2","2"]
["Napájení","Fáze","","","","3~","3~","3~"]
["","Napájení-=-Frekvence","","Frekvence","","50","50","50"]
["","Napájení-=-Napětí","","Napětí","","380-415","380-415","380-415"]
["Proud - 50 Hz","Proud - 50 Hz-=-Maximální proud na pojistkách (MFA)","","Proud - 50 Hz-=-Maximální proud na pojistkách (MFA)-=-A","","","16"]
["Poznámky","","","","","","(1) - V souladu s ENER Lot 21","(1) - V souladu s ENER Lot 21"]
["Hmotnost","Jednotka","","","kg","70","","77"]
["Kompresor","Typ","","","","Hermeticky utěsněný rotační kompresor","","Hermeticky utěsněný rotační kompresor"]
["Chladivo","Vliv na globální oteplování (GWP)","","","","675","","675"]
["Připojovací rozměry","Plyn","","Vnější průměr","mm","15.9","","15.9"]
["Proud – 50&nbsp;Hz","Proud – 50&nbsp;Hz-=-Max. proudová hodnota pojistky (MFA)-=-A","","","A","16","","16"]