{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":60,"n_cols":9,"rows_kept":60,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWYA-DW1P-H-"]
[]
[]
[]
[]
["","","","","","EWYA009DAW1P-H-","EWYA011DAW1P-H-","EWYA014DAW1P-H-","EWYA016DAW1P-H-"]
["Hladina akustického tlaku","Chlazení","","Jm.","dBA","44.0","47.7","50.8","51.0"]
["Komponenty hydrauliky","Expanzní nádoba","","Objem","l","8","8","8","8"]
["Provozní rozsah","Vzduchová strana","Chlazení","Min.","°CST","10","10","10","10"]
["","","","Max.","°CST","43","43","43","43"]
["","","Vytápění","Max.","°CST","25","25","25","25"]
["","","","Min.","°CST","-25","-25","-25","-25"]
["","Strana vody","Vytápění","Min.","°CST","9 (7)","9 (7)","9 (7)","9 (7)"]
["","","","Max.","°CST","60 (7)","60 (7)","60 (7)","60 (7)"]
["","","Chlazení","Max.","°CST","22","22","22","22"]
["","","","Min.","°CST","5","5","5","5"]
["Náplň chladiva","Na okruh","","","kg","3.80","3.80","3.80","3.80"]
["","Refrigerant charge-=-Per circuit-=-TCO2Eq","","","TCO2Eq","2.6","2.6","2.6","2.6"]
["Kompresor","Typ","","","","Hermeticky utěsněný swing kompresor řízený invertorem","Hermeticky utěsněný swing kompresor řízený invertorem","Hermeticky utěsněný swing kompresor řízený invertorem","Hermeticky utěsněný swing kompresor řízený invertorem"]
["","Startovací metoda_","","","","Poháněný měničem","Poháněný měničem","Poháněný měničem","Poháněný měničem"]
["","Množství_","","","","1","1","1","1"]
["Vzduchový výměník tepla","Typ","","","","Vysoce účinný typ lamel a trubek s integrovaným dochlazovačem","Vysoce účinný typ lamel a trubek s integrovaným dochlazovačem","Vysoce účinný typ lamel a trubek s integrovaným dochlazovačem","Vysoce účinný typ lamel a trubek s integrovaným dochlazovačem"]
["Hmotnost","Jednotka","","","kg","147","147","147","147"]
["EER","","","","","3.35 (1), 5.34 (2)","3.26 (1), 5.31 (2)","3.16 (1), 5.04 (2)","3.06 (1), 4.74 (2)"]
["Chladivo","Vliv na globální oteplování (GWP)","","","","675.0","675.0","675.0","675.0"]
["","Typ","","","","R-32","R-32","R-32","R-32"]
["","Okruhy","","Množství","","1","1","1","1"]
["","Řízení","","","","Elektronický expanzní ventil","Elektronický expanzní ventil","Elektronický expanzní ventil","Elektronický expanzní ventil"]
["Motor ventilátoru","Otáčky","Chlazení","Jm.","ot./min","500","550","650","650"]
["","","Vytápění","Jm.","ot./min","400","450","550","650"]
["Chladicí výkon","Jm.","","","kW","9.35 (1), 9.10 (2)","11.6 (1), 11.5 (2)","12.8 (1), 12.7 (2)","14.0 (1), 15.3 (2)"]
["Vodní výměník tepla","Objem vody","","","l","2","2","2","2"]
["","Min. objem vody v systému","","","l","50 (6)","50 (6)","50 (6)","50 (6)"]
["","Typ","","","","Deskový výměník tepla","Deskový výměník tepla","Deskový výměník tepla","Deskový výměník tepla"]
["Příkon","Chlazení","","Jm.","kW","2.79 (1), 1.71 (2)","3.56 (1), 2.17 (2)","4.06 (1), 2.51 (2)","4.58 (1), 3.24 (2)"]
["","Vytápění","","Jm.","kW","1.91 (3), 2.43 (4)","2.18 (3), 2.68 (4)","2.46 (3), 3.42 (4)","3.53 (3), 4.56 (4)"]
["Sound power level","Chlazení","","Jm.","dBA","65.5","67.0","69.0","69.0"]
["COP","","","","","4.91 (3), 3.71 (4)","4.83 (3), 3.66 (4)","4.87 (3), 3.64 (4)","4.53 (3), 3.51 (4)"]
["Rozměry","Jednotka","","Šířka","mm","1,380","1,380","1,380","1,380"]
["","","","Hloubka","mm","460","460","460","460"]
["","","","Výška","mm","870","870","870","870"]
["Řízení kapacity","Metoda","","","","Proměnná (invertor)","Proměnná (invertor)","Proměnná (invertor)","Proměnná (invertor)"]
["Prostorové vytápění","Výstup vody 55 °C v průměrném podnebí","Obecně","Třída celoroční účinnosti prostorového vytápění","","A++","A++","A++","A++"]
["","","","ηs (Celoroční účinnost prostorového vytápění)","%","135","132","134","132"]
["","","","SCOP","","3.44","3.37","3.42","3.37"]
["Ventilátor","Průtok vzduchu","Vytápění","Jm.","m³/min","48.0","55.8","70.4","85.0"]
["","","Chlazení","Jm.","m³/min","63","70","85","85"]
["Topný výkon","Jm.","","","kW","9.37 (3), 9.00 (4)","10.6 (3), 9.82 (4)","12.0 (3), 12.5 (4)","16.0 (3), 16.0 (4)"]
["Kompresor","Startovací metoda_","","","","Měnič","Měnič","Měnič","Měnič"]
["Power supply","Fáze","","","","3~","3~","3~","3~"]
["","Frekvence","","","Hz","50","50","50","50"]
["","Označení","","","","W1","W1","W1","W1"]
["","Napětí","","","V","400","400","400","400"]
["Poznámky","","","","","(1) - Chlazení: EW 12 °C; LW 7 °C; podmínky okolního prostředí: 35 °CDB","(1) - Chlazení: EW 12 °C; LW 7 °C; podmínky okolního prostředí: 35 °CDB","(1) - Chlazení: EW 12 °C; LW 7 °C; podmínky okolního prostředí: 35 °CDB","(1) - Chlazení: EW 12 °C; LW 7 °C; podmínky okolního prostředí: 35 °CDB"]
["","","","","","(2) - Chlazení: EW 23 °C; LW 18 °C; podmínky okolního prostředí: 35 °CDB","(2) - Chlazení: EW 23 °C; LW 18 °C; podmínky okolního prostředí: 35 °CDB","(2) - Chlazení: EW 23 °C; LW 18 °C; podmínky okolního prostředí: 35 °CDB","(2) - Chlazení: EW 23 °C; LW 18 °C; podmínky okolního prostředí: 35 °CDB"]
["","","","","","(3) - Betingelse: Ta DB/WB 7 °C/6 °C - LWC 35 °C (DT = 5 °C)","(3) - Betingelse: Ta DB/WB 7 °C/6 °C - LWC 35 °C (DT = 5 °C)","(3) - Betingelse: Ta DB/WB 7 °C/6 °C - LWC 35 °C (DT = 5 °C)","(3) - Betingelse: Ta DB/WB 7 °C/6 °C - LWC 35 °C (DT = 5 °C)"]
["","","","","","(4) - Podmínka: Ta DB/WB 7 °C/6 °C - LWC 45℃ (DT = 5 °C)","(4) - Podmínka: Ta DB/WB 7 °C/6 °C - LWC 45℃ (DT = 5 °C)","(4) - Podmínka: Ta DB/WB 7 °C/6 °C - LWC 45℃ (DT = 5 °C)","(4) - Podmínka: Ta DB/WB 7 °C/6 °C - LWC 45℃ (DT = 5 °C)"]
["","","","","","(5) - Podle EN14825","(5) - Podle EN14825","(5) - Podle EN14825","(5) - Podle EN14825"]
["","","","","","(6) - Závisí na provozním režimu, podrobnosti jsou uvedeny v instalační příručce.","(6) - Závisí na provozním režimu, podrobnosti jsou uvedeny v instalační příručce.","(6) - Závisí na provozním režimu, podrobnosti jsou uvedeny v instalační příručce.","(6) - Závisí na provozním režimu, podrobnosti jsou uvedeny v instalační příručce."]
["","","","","","(7) - Podrobnosti viz výkres provozních rozsahů","(7) - Podrobnosti viz výkres provozních rozsahů","(7) - Podrobnosti viz výkres provozních rozsahů","(7) - Podrobnosti viz výkres provozních rozsahů"]