{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":62,"n_cols":14,"rows_kept":62,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FXFA-A"]
[]
[]
[]
[]
["","","","","","FXFA20A2VEB","FXFA25A2VEB","FXFA32A2VEB","FXFA40A2VEB","FXFA50A2VEB","FXFA63A2VEB","FXFA80A2VEB","FXFA100A2VEB","FXFA125A2VEB"]
["Chladicí výkon","Celkový výkon","","Při vysokých otáčkách ventilátoru","kW","2.20","2.80","3.60","4.50","5.60","7.10","9.00","11.20","14.00"]
["Topný výkon","Celkový výkon","","Při vysokých otáčkách ventilátoru","kW","2.50","3.20","4.00","5.00","6.30","8.00","10.00","12.50","16.00"]
["Příkon - 50Hz","Chlazení","","Při vysokých otáčkách ventilátoru","kW","0.017 (1)","0.017 (1)","0.017 (1)","0.018 (1)","0.023 (1)","0.028 (1)","0.045 (1)","0.078 (1)","0.103 (1)"]
["","Vytápění","","Při vysokých otáčkách ventilátoru","kW","0.017 (1)","0.017 (1)","0.017 (1)","0.018 (1)","0.023 (1)","0.028 (1)","0.045 (1)","0.078 (1)","0.103 (1)"]
["Rozměry","Jednotka","","Výška","mm","204","204","204","204","204","204","246","246","288"]
["","","","Šířka","mm","840","840","840","840","840","840","840","840","840"]
["","","","Hloubka","mm","840","840","840","840","840","840","840","840","840"]
["Hmotnost","Jednotka","","","kg","18","18","18","19","21","21","24","24","26"]
["Opláštění","Materiál","","","","Pozinkovaný ocelový plech","Pozinkovaný ocelový plech","Pozinkovaný ocelový plech","Pozinkovaný ocelový plech","Pozinkovaný ocelový plech","Pozinkovaný ocelový plech","Pozinkovaný ocelový plech","Pozinkovaný ocelový plech","Pozinkovaný ocelový plech"]
["Ventilátor","Průtok vzduchu – 50Hz","Chlazení","Při vysokých otáčkách ventilátoru","m³/min","12.8","12.8","12.8","14.8","15.1","16.6","23.3","28.8","33.0"]
["","","","Při nízkých otáčkách ventilátoru","m³/min","8.9","8.9","8.9","10.4","10.7","10.7","13.8","13.8","20.6"]
["Chladivo","Typ","","","","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32"]
["","Vliv na globální oteplování (GWP)","","","","675","675","675","675","675","675","675","675","675"]
["Hladina akustického výkonu","Chlazení","","Při vysokých otáčkách ventilátoru","dBA","49.0","49.0","49.0","51.0","51.0","53.0","55.0","60.0","61.0"]
["Hladina akustického tlaku","Chlazení","","Při vysokých otáčkách ventilátoru","dBA","31.0","31.0","31.0","33.0","33.0","35.0","38.0","43.0","45.0"]
["","","","Při středních otáčkách ventilátoru","dBA","29.0","29.0","29.0","31.0","31.0","33.0","34.0","37.0","41.0"]
["","","","Při nízkých otáčkách ventilátoru","dBA","28.0","28.0","28.0","29.0","29.0","30.0","30.0","30.0","36.0"]
["","Vytápění","","Při vysokých otáčkách ventilátoru","dBA","31.0","31.0","31.0","33.0","33.0","35.0","38.0","43.0","45.0"]
["","","","Při středních otáčkách ventilátoru","dBA","29.0","29.0","29.0","31.0","31.0","33.0","34.0","37.0","41.0"]
["","","","Při nízkých otáčkách ventilátoru","dBA","28.0","28.0","28.0","29.0","29.0","30.0","30.0","30.0","36.0"]
["Připojovací rozměry","Kapalina","","Typ","","Rozlisované připojení","Rozlisované připojení","Rozlisované připojení","Rozlisované připojení","Rozlisované připojení","Rozlisované připojení","Rozlisované připojení","Rozlisované připojení","Rozlisované připojení"]
["","","","Vnější průměr","mm","6","6","6","6","6","6","6","10","10"]
["","Plyn","","Typ","","Rozlisované připojení","Rozlisované připojení","Rozlisované připojení","Rozlisované připojení","Rozlisované připojení","Rozlisované připojení","Rozlisované připojení","Rozlisované připojení","Rozlisované připojení"]
["","","","Vnější průměr","mm","9.52","9.52","9.52","12.7","12.7","12.7","12.7","15.9","15.9"]
["","Odvod kondenzátu","","","","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)"]
["Dekorační panel","Model","","","","BYCQ140E2W1, BYCQ140E2W1W, BYCQ140E2W1B","BYCQ140E2W1, BYCQ140E2W1W, BYCQ140E2W1B","BYCQ140E2W1, BYCQ140E2W1W, BYCQ140E2W1B","BYCQ140E2W1, BYCQ140E2W1W, BYCQ140E2W1B","BYCQ140E2W1, BYCQ140E2W1W, BYCQ140E2W1B","BYCQ140E2W1, BYCQ140E2W1W, BYCQ140E2W1B","BYCQ140E2W1, BYCQ140E2W1W, BYCQ140E2W1B","BYCQ140E2W1, BYCQ140E2W1W, BYCQ140E2W1B","BYCQ140E2W1, BYCQ140E2W1W, BYCQ140E2W1B"]
["","Rozměry","","Výška","mm","65","65","65","65","65","65","65","65","65"]
["","","","Šířka","mm","950","950","950","950","950","950","950","950","950"]
["","","","Hloubka","mm","950","950","950","950","950","950","950","950","950"]
["","Hmotnost","","","kg","5.5","5.5","5.5","5.5","5.5","5.5","5.5","5.5","5.5"]
["Dekorační panel 2","Model","","","","BYCQ140E2GFW1, BYCQ140E2GFW1B","BYCQ140E2GFW1, BYCQ140E2GFW1B","BYCQ140E2GFW1, BYCQ140E2GFW1B","BYCQ140E2GFW1, BYCQ140E2GFW1B","BYCQ140E2GFW1, BYCQ140E2GFW1B","BYCQ140E2GFW1, BYCQ140E2GFW1B","BYCQ140E2GFW1, BYCQ140E2GFW1B","BYCQ140E2GFW1, BYCQ140E2GFW1B","BYCQ140E2GFW1, BYCQ140E2GFW1B"]
["","Rozměry","","Výška","mm","148","148","148","148","148","148","148","148","148"]
["","","","Šířka","mm","950","950","950","950","950","950","950","950","950"]
["","","","Hloubka","mm","950","950","950","950","950","950","950","950","950"]
["","Hmotnost","","","kg","10.3","10.3","10.3","10.3","10.3","10.3","10.3","10.3","10.3"]
["Dekorační panel 3","Model","","","","BYCQ140E2P, BYCQ140E2PB","BYCQ140E2P, BYCQ140E2PB","BYCQ140E2P, BYCQ140E2PB","BYCQ140E2P, BYCQ140E2PB","BYCQ140E2P, BYCQ140E2PB","BYCQ140E2P, BYCQ140E2PB","BYCQ140E2P, BYCQ140E2PB","BYCQ140E2P, BYCQ140E2PB","BYCQ140E2P, BYCQ140E2PB"]
["","Rozměry","","Výška","mm","106","106","106","106","106","106","106","106","106"]
["","","","Šířka","mm","950","950","950","950","950","950","950","950","950"]
["","","","Hloubka","mm","950","950","950","950","950","950","950","950","950"]
["","Hmotnost","","","kg","6.5","6.5","6.5","6.5","6.5","6.5","6.5","6.5","6.5"]
["Vzduchový filtr","Typ","","","","Pryskyřicová síť","Pryskyřicová síť","Pryskyřicová síť","Pryskyřicová síť","Pryskyřicová síť","Pryskyřicová síť","Pryskyřicová síť","Pryskyřicová síť","Pryskyřicová síť"]
["Standardní příslušenství","Washer for hanger bracket","","","","8","8","8","8","8","8","8","8","8"]
["","Wire clamp material","","","","7","7","7","7","7","7","7","7","7"]
["","Clamp for drain hose","","","","1","1","1","1","1","1","1","1","1"]
["","Clamps","","","","1","1","1","1","1","1","1","1","1"]
["","Drain hose","","","","1","1","1","1","1","1","1","1","1"]
["","Installation and operation manual","","","","1","1","1","1","1","1","1","1","1"]
["","Installation guide","","","","1","1","1","1","1","1","1","1","1"]
["","Insulation for fitting","","","","2","2","2","2","2","2","2","2","2"]
["","Screws","","","","4","4","4","4","4","4","4","4","4"]
["","Sealing pads","","","","1","1","1","1","1","1","1","1","1"]
["Napájení","Fáze","","","","1~","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Frekvence","","","Hz","50/60","50/60","50/60","50/60","50/60","50/60","50/60","50/60","50/60"]
["","Napětí","","","V","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220"]
["Proud – 50&nbsp;Hz","Proud – 50&nbsp;Hz-=-Max. proudová hodnota pojistky (MFA)-=-A","","","A","6","6","6","6","6","6","6","6","6"]
["Poznámky","","","","","(1) - Hodnoty platí pro tovární nastavení.","(1) - Hodnoty platí pro tovární nastavení.","(1) - Hodnoty platí pro tovární nastavení.","(1) - Hodnoty platí pro tovární nastavení.","(1) - Hodnoty platí pro tovární nastavení.","(1) - Hodnoty platí pro tovární nastavení.","(1) - Hodnoty platí pro tovární nastavení.","(1) - Hodnoty platí pro tovární nastavení.","(1) - Hodnoty platí pro tovární nastavení."]