{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":42,"n_cols":6,"rows_kept":42,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","LRYEQ-AY"]
[]
[]
[]
[]
["","","","","","LRYEQ16A7Y1"]
["Standardní příslušenství","Příručka pro instalaci","","","","1"]
["","Manuální ovládání","","","","1"]
["","Propojovací potrubí","","","","1"]
["","Štítek chladiva pro předpisy k F-plynům","","","","1"]
["","Štítek náplně chladiva","","","","1"]
["","Vícejazyčné štítky pro fluorované skleníkové plyny","","","","1"]
["Hmotnost","Jednotka","","","kg","370"]
["Refrigerant","Charge","","","TCO2Eq","24.0"]
["","GWP","","","","2,087.5"]
["","Náplň","","","kg","11.5"]
["","Typ","","","","R-410A"]
["Motor ventilátoru","Výkon","","","W","750"]
["","Pohon","","","","Přímý pohon"]
["Tepelný výměník","Typ","","","","Křížová lamela spirály"]
["Rozměry","Jednotka","","Šířka","mm","1,240"]
["","","","Hloubka","mm","765"]
["","","","Výška","mm","1,680"]
["Opláštění","Barva","","","","Slonovinová"]
["Fan","Type","","","","Ventilátor oběžného kola"]
["","Průtok vzduchu","Chlazení","Jm.","m³/min","230"]
["","Množství","","","","2"]
["Power supply","Fáze","","","","3~"]
["","Frekvence","","","Hz","50"]
["","Napětí","","","V","380-415"]
["Poznámky","","","","","(1) - Prioritní režim chlazení: vnitřní teplota 27°CDB, 19°CWB; vnější teplota 32°CDB; délka potrubí: 7,5m; rozdíl hladin: 0m"]
["","","","","","(2) - Prioritní režim chlazení: výparná teplota -10℃; vnější teplota 32°CDB; Sání SH: 10℃"]
["","","","","","(3) - 100% režim zpětného získávání tepla: vnitřní teplota 20°CDB; vnější teplota 7°CDB, 6°CWB; zátěž chlazení 18kW; délka potrubí: 7,5m; rozdíl hladin: 0m"]
["","","","","","(4) - Teplota nasycení je ekvivalentní sacímu tlaku (strana chlazení): -10°C (v podmínkách chlazení); kapacita připojení pro vnitřní klimatizaci: 10HP, když je zpětné získávání tepla 100%"]
["","","","","","(5) - Kompresor 1"]
["","","","","","(6) - Kompresor 2"]
["","","","","","(7) - Kompresor 3"]
["","","","","","(8) - Náplň jednotky ze závodu"]
["","","","","","(9) - Nainstalujte lapač oleje po 5m od venkovní jednotky"]
["","","","","","(10) - Podrobnosti viz výkres provozních rozsahů"]
["","","","","","(11) - Více podrobností o standardním příslušenství je uvedeno v instalační/provozní příručce"]
["","","","","","(12) - Obsahuje fluorované skleníkové plyny"]