{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":41,"n_cols":13,"rows_kept":41,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RZAG-NY1"]
[]
[]
[]
[]
["","","","","","RZAG71N2Y1B","RZAG71N7Y1B","RZAG100N7Y1B","RZAG100N2Y1B","RZAG125N2Y1B","RZAG125N7Y1B","RZAG140N7Y1B","RZAG140N2Y1B"]
["Rozměry","Jednotka","","Výška","mm","870","870","870","870","870","870","870","870"]
["","","","Šířka","mm","1100","1100","1100","1100","1100","1100","1100","1100"]
["","","","Hloubka","mm","460","460","460","460","460","460","460","460"]
["Hmotnost","Jednotka","","","kg","81","81","85","85","94","94","94","94"]
["Kompresor","Typ","","","","Hermeticky utěsněný rotační kompresor","Hermeticky utěsněný rotační kompresor","Hermeticky utěsněný rotační kompresor","Hermeticky utěsněný rotační kompresor","Hermeticky utěsněný rotační kompresor","Hermeticky utěsněný rotační kompresor","Hermeticky utěsněný rotační kompresor","Hermeticky utěsněný rotační kompresor"]
["Provozní rozsah","Chlazení","Okolí","Min.","°CST","-20","-20","-20","-20","-20","-20","-20","-20"]
["","","","Max.","°CST","52","52","52","52","52","52","52","52"]
["","Vytápění","Okolí","Min.","° CWB","-20","-20","-20","-20","-20","-20","-20","-20"]
["","","","Max.","° CWB","18","18","18","18","18","18","18","18"]
["Hladina akustického výkonu","Chlazení","","","dBA","64","64","66","66","69","69","70","70"]
["","Vytápění","","","dBA","","","","","68 (1)","68 (1)","71 (1)","71 (1)"]
["Hladina akustického tlaku","Chlazení","","Jm.","dBA","46","46","47","47","49","49","50","50"]
["","Vytápění","","Jm.","dBA","48","48","50","50","52","52","52","52"]
["Chladivo","Typ","","","","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32"]
["","Náplň","","","kg","3.20","3.2","3.2","3.20","3.70","3.7","3.7","3.70"]
["","Vliv na globální oteplování (GWP)","","","","675","675","675","675","675","675","675","675"]
["","Náplň","","","tCO2Eq","2.16","2.16","2.16","2.16","2.50","2.5","2.5","2.50"]
["Připojovací rozměry","Kapalina","","Vnější průměr","mm","10","10","10","10","10","10","10","10"]
["","Plyn","","Vnější průměr","mm","15.9","15.9","15.9","15.9","15.9","15.9","15.9","15.9"]
["Spoje potrubí","Délka potrubí","Max.","OU - IU","m","55","55","85","85","85","85","85","85"]
["","","Systém","Ekvivalent","m","75","75","100","100","100","100","100","100"]
["","","","Bez náplně","m","40","40","40","40","40","40","40","40"]
["","Doplňková náplň chladiva","","","kg/m","Viz instalační příručka","Viz instalační příručka","Viz instalační příručka","Viz instalační příručka","Viz instalační příručka","Viz instalační příručka","Viz instalační příručka","Viz instalační příručka"]
["","Rozdíl hladin","IU - OU","Max.","m","30","30","30","30","30","30","30","30"]
["","","IU - IU","Max.","m","0.5","0.5","0.5","0.5","0.5","0.5","0.5","0.5"]
["Standardní příslušenství","Installation manual","","","","1","1","1","1","1","1","1","1"]
["","Refrigerant label for F-gas regulation","","","","1","1","1","1","1","1","1","1"]
["","General safety precautions","","","","1","1","1","1","1","1","1","1"]
["","Peel off F-gas label","","","","1","1","1","1","1","1","1","1"]
["","Tie-wraps","","","","2","2","2","2","2","2","2","2"]
["Napájení","Fáze","","","","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Frekvence","","","Hz","50","50","50","50","50","50","50","50"]
["","Napětí","","","V","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415"]
["Proud – 50&nbsp;Hz","Proud – 50&nbsp;Hz-=-Max. proudová hodnota pojistky (MFA)-=-A","","","A","16","16","16","16","16","16","16","16"]
["Poznámky","","","","","","","","","(1) - V souladu s ENER Lot 21","(1) - Vsouladu sENER Lot 21","(1) - V souladu s ENER Lot 21","(1) - V souladu s ENER Lot 21"]